## Sheet1
Address (Register) |  | Input Register Parameter |  |  |  | Modbus Protocol Start Address Hex
| Description |  | Length (bytes) | Data Format | Units | Hi | Lo
30001 | Phase 1 line to neutral volts. |  | 4 | Float | V | 0 | 00
30003 | Phase 2 line to neutral volts. |  | 4 | Float | V | 0 | 02
30005 | Phase 3 line to neutral volts. |  | 4 | Float | V | 0 | 04
30007 | Phase 1 current. |  | 4 | Float | A | 0 | 06
30009 | Phase 2 current. |  | 4 | Float | A | 0 | 08
30011 | Phase 3 current. |  | 4 | Float | A | 0 | 0A
30013 | Phase 1 active power. |  | 4 | Float | W | 0 | 0C
30015 | Phase 2 active power. |  | 4 | Float | W | 0 | 0E
30017 | Phase 3 active power. |  | 4 | Float | W | 0 | 10
30019 | Phase 1 apparent power. |  | 4 | Float | VA | 0 | 12
30021 | Phase 2 apparent power. |  | 4 | Float | VA | 0 | 14
30023 | Phase 3 apparent power. |  | 4 | Float | VA | 0 | 16
30025 | Phase 1 reactive power. |  | 4 | Float | VAr | 0 | 18
30027 | Phase 2 reactive power. |  | 4 | Float | VAr | 0 | 1A
30029 | Phase 3 reactive power. |  | 4 | Float | VAr | 0 | 1C
30031 | Phase 1 power factor (1). |  | 4 | Float | None | 0 | 1E
30033 | Phase 2 power factor (1). |  | 4 | Float | None | 0 | 20
30035 | Phase 3 power factor (1). |  | 4 | Float | None | 0 | 22
30043 | Average line to neutral volts. |  | 4 | Float | V | 0 | 2A
30047 | Average line current. |  | 4 | Float | A | 0 | 2E
30049 | Sum of line currents. |  | 4 | Float | A | 0 | 30
30053 | Total system power. |  | 4 | Float | W | 0 | 34
30057 | Total system volt amps. |  | 4 | Float | VA | 0 | 38
30061 | Total system VAr. |  | 4 | Float | VAr | 0 | 3C
30063 | Total system power factor (1 ). |  | 4 | Float | None | 0 | 3E
30071 | Frequency of supply voltages. |  | 4 | Float | Hz | 0 | 46
30073 | Import active energy |  | 4 | Float | kWh | 0 | 48
30075 | Export active energy |  | 4 | Float | kWh | 0 | 4A
30201 | Line 1 to Line 2 volts. |  | 4 | Float | V | 0 | C8
30203 | Line 2 to Line 3 volts. |  | 4 | Float | V | 0 | CA
30205 | Line 3 to Line 1 volts. |  | 4 | Float | V | 0 | CC
30207 | Average line to line volts. |  | 4 | Float | V | 0 | CE
30225 | Neutral current. |  | 4 | Float | A | 0 | E0
30343 | Total active Energy (2) |  | 4 | Float | kWh | 1 | 56
30345 | Total reactive energy |  | 4 | Float | kVArh | 1 | 58
30385 | resettable total active energy |  | 4 | Float | kWh | 1 | 80
30387 | Resettable total reactive energy |  | 4 | Float | kVarh | 1 | 82
30389 | resettable import active energy |  | 4 | Float | kWh | 1 | 84
30391 | resettable export active energy |  | 4 | Float | kWh | 1 | 86
30397 | Net kWh (Import - Export) |  | 4 | Float | kWh | 1 | 8C
31281 | Total import active power |  | 4 | Float | W | 5 | 00
31283 | Total export active power |  | 4 | Float | W | 5 | 02